Case Study
Implementing eMaintenance using iSCADA technology for Wisma Persekutuan Melaka
By Nurhaizan
JKR Mekanikal Melaka
Published by permission and courtesy of JKR mekanikal Meleka.

---
Background
The Fire Protection System in Wisma Persekutuan Melaka was upgraded in December 2003
At the same time, a Web-based SCADA (iSCADA) system was installed to monitor the Fire Alarm, Hose Reel, Sprinkler, Chiller and Lift Systems.
We implemented Electronic Maintenance (eMaintenance) to enhance our Maintenance Management process

---
How iSCADA works
A Gateway collects failure events from our equipment and transmits them to a server on the Internet.
When a failure occurs, technicians automatically receive an SMS and email
JKR and the FM contractor can access the data in real time from any PC
Internet Server
Gateway
User

---
Site 1
Tel Line
Site N
Mobile Alerts
Online Reports / Statistics
Real-time Monitor / Alarm
Internet
iSCADA Server
Embedded
Internet
Gateway
Embedded
Internet
Gateway
Architecture
[Speaker Notes: iSCADA system architecture]

---
Monitor by System (Data from JKR melaka)
See Status of ALL systems on the same screen
Systems in good condition are in Yellow Folder
Systems with Failure Events are in RED Folder
Click on RED folder to see details of Failures

---
Monitor by Location (Data from JKR melaka)
See Status of ALL sites/buildings at once
Buildings in good condition are in Yellow Folder
Buildings with Failure Events are in RED Folder
Click on RED folder to see details of Failures

---
Site 1
Melaka
Site 2
Perak
Site 3
Johor
Internet
iSCADA Server
Global Reach
Kawalselia
[Speaker Notes: Kawalselia at Headquarters is able to see data from ALL buildings in ALL states]

---
Real Time Monitoring screen shot showing that a Fault occurred in the Fire Alarm System on
26 May 2005 at 7:54 pm
An email and SMS was sent to Nurhaizan and Zulhelmi when the failure occurred

---
Reporting screen shot showing that the same fault kept repeating since 13th May 2005

---
Statistics screen shot showing overall system availability from 1st Jan 2004 to 31st Dec 2004
Overall Functionality Index (Up Time) = 98.24%
Fire Alarm Up Time was lowest at 88.3%
Total Down Time of all systems = 511.72 Hours

---
How JKR has benefited from implementation of eMaintenance
Transparency
Everything was recorded automatically without human intervention. Reports & statistics are available online to top management in real time.
Efficiency
Reduces manpower for fault detection and paper work
Availability
Automatic detection and SMS enables quick actions to be taken. This improves the overall availability of our systems.

---
Reporting Concept: eMaintenance Vs Conventional Maintenance
Conventional
Maintenance
Electronic
Maintenance
Central Authority
Central Authority
Reports
Query /Login
Information
Lower Authorities
Lower Authorities
Reports
Lower Authorities
Lower Authorities
Reports
Assets /
Data Source
Assets /
Data Source
[Speaker Notes: .]

---
        Reactive & Predictive Components of eMaintenance
Reactive Maintenance:
React to a system failure, and attempt to restore normal functionality in the shortest time possible.
iSCADA’s role in Reactive Maintenance:-
Detecting Failures automatically, and sending alerts to technicians instantly and automatically by email & SMS.
Logs all events and produces statistical analysis that can point to the root cause of problems (See next slide)
Predictive Maintenance:
Anticipate system failures before they happen by using Condition Monitoring tools
iSCADA’s role in Predictive Maintenance:-
(1) Monitoring analogue signals from the site in real time
(2) Analyzing Trending data to detect abnormal behavior.

---
 iSCADA helps point to root cause of failures
After the Fire Protection system at Wisma Persekutuan Melaka was upgraded, we used the iSCADA system to monitor the performance of the new installation.
We found that there was over 500 events reported by the Sprinkler System.
We drill deeper into the iSCADA statistical analysis report and it showed that the Jockey Pump ran for 443 times in a very short period of time, which is not normal.
This indicated a leak in the piping system, which was subsequently fixed by the contractor.
Due to Leaks in the Sprinkler System piping
Screenshot of actual site data from JKR Melaka

---
 iSCADA helps in Predictive Maintenance
Conditioning Monitoring allows maintenance engineers to detect abnormal behavior. Action can then be taken to prevent an actual failure.
Eg 1. If a temperature sensor is embedded into the shaft of the Lift Motor, the temperature profile may indicate abnormalities in bearings or load.
Eg 2. Taking periodic readings of peak current consumption of a compressor, and observing the trend over a period of time may point to deteriorating efficiency.

---
Moving Forward
Implement eMaintenance in all JKR buildings state-wide and nationwide
This allows consolidation of maintenance management data and central supervision
Performance of FM contractors can be monitored objectively with Key Performance Indicators (KPIs)
Ensure that Maintenance budgets are managed prudently
Enables JKR to perform Predictive Maintenance